HOME AUTOMATION, INC.

Control & Security System

Installation Manual

Document Number 20I00

December, 2009

Copyright © 2001-2009 Home Automation, Inc.

All Rights Reserved

CONTENTS

INTRODUCTION	1

PLANNING	1

INSTALLATION	2

CONTROLLER HOOKUP	2

ABOUT SECURITY ZONES	4

BURGLAR ZONE HOOKUPS	4

ABOUT FIRE ZONES	5

TWO-WIRE SMOKE DETECTORS	6

FOUR-WIRE SMOKE DETECTORS	6

TELEPHONE CONNECTIONS	9

DIGITAL SUBSCRIBER LINE (DSL) CONNECTIONS	9

LCD CONSOLE HOOKUP	11

CONSOLE SETUP	12

CONSOLE ADDRESS	12

SOUNDER	12

KEY CLICK	12

KEY BACKLIGHT	12

VIEWING ADJUSTMENT	12

LANGUAGE	12

EXIT SETUP MODE	12

SOUNDER OUTPUTS	14

INTERIOR SOUNDER HOOKUP	14

EXTERIOR SOUNDER HOOKUP	14

CONTROLLER OUTPUTS	16

RESET OUTPUTS	16

OUTPUT APPLICATIONS	16

GENERAL PURPOSE SWITCHING APPLICATIONS	16

SOUNDER TRIGGERING	16

COMMUNICATOR OUTPUTS	17

"ARMED" AND "OK TO ARM"	17

SWITCHED OUTPUT	17

HAI COMMUNICATING THERMOSTATS	17

REMOTE ARM/DISARM SWITCH	17

HAI THERMOSTATS	19

PROGRAMMABLE ENERGY SAVER MODULES	20

TEMPERATURE, OUTDOOR TEMPERATURE, AND HUMIDITY	21

BUILT-IN SERIAL PORTS	23

BUILT-IN ETHERNET PORT	24

CONTROLLER IP ADDRESS, PORT NUMBER, AND ENCRYPTION KEY	24

CONTROLLER IP ADDRESS	25

CONTROLLER PORT NUMBER	25

ENCRYPTION KEY	25

ETHERNET CONNECTIONS	25

CONNECTING TO NETWORK VIA PC ACCESS	26

SYSTEM POWER UP PROCEDURE	28

CONSOLE CHECK OUT	28

TELEPHONE CHECK OUT	28

BURGLAR ZONE CHECK OUT	29

FIRE ZONE CHECK OUT	29

CUSTOMER CHECKOUT	29

IN CASE OF TROUBLE	30

CONSOLES	30

CONTROLLER	30

DIGITAL COMMUNICATOR	32

DESCRIPTION OF CONTACT ID	32

DESCRIPTION OF 4/2 and 3/1 FORMAT	33

OPENING AND CLOSING REPORTS	33

ZONE TYPES	34

LATCHING ZONE TYPES	34

DESCRIPTION OF ZONE TYPES	34

MISCELLANEOUS	37

INSTALLER CODE	37

ENABLE PC ACCESS	37

PC ACCESS CODE	37

RESET SYSTEM EEPROM	37

RESET SYSTEM RAM	38

ETHERNET MAC ADDRESS	38

EXPANSION	38

MODULE 1 TYPE	38

MODULE 2 TYPE - MODULE 4 TYPE	39

SERIAL 1 RATE	39

SERIAL 1 FUNCTION	39

SERIAL 2 - SERIAL 5 RATE	39

SERIAL 2 FUNCTION	39

SERIAL 3 FUNCTION	40

SERIAL 4 - SERIAL 5 FUNCTION	40

SERIAL 6 RATE	40

SPECIFICATIONS	41

UNDERWRITER'S LABORATORIES (UL) INSTALLATION REQUIREMENTS	42

24-HOUR STANDBY BATTERY CAPACITY	43

SMOKE DETECTOR INSTALLATION GUIDELINES	44

APPENDIX A – CONTACT ID REPORTING FORMAT	45

FIGURES

FIGURE 1 - CONTROLLER HOOKUP	3

FIGURE 2 - OVERALL CONNECTIONS DIAGRAM	5

FIGURE 3 - TWO-WIRE FIRE ZONE CONNECTIONS	7

FIGURE 4 - FOUR-WIRE FIRE ZONE CONNECTIONS	8

FIGURE 5 - RJ31X JACK CONNECTIONS	10

FIGURE 6 – DSL SPLITTER CONNECTIONS	11

FIGURE 7 - CONSOLE CONNECTIONS	13

FIGURE 8 - SOUNDER CONNECTIONS	15

FIGURE 9 - RESETTING CONTROLLER OUTPUTS	16

FIGURE 10 - REMOTE KEYSWITCH CONNECTIONS	18

FIGURE 11 - HAI THERMOSTAT CONNECTIONS	19

FIGURE 12 - TEMPERATURE / HUMIDITY SENSOR CONNECTIONS	21

FIGURE 13 - PESM CONNECTIONS	22

FIGURE 14 - RS-232 CONNECTIONS	23

FIGURE 15 - RS-485 CONNECTIONS	24

FIGURE 16 - LOCAL NETWORK	26

FIGURE 17 - LOCAL / WIDE AREA NETWORK	27

FIGURE 18 - 24-HOUR STANDBY CONNECTIONS	60

# INTRODUCTION

This installation guide is intended as an aid to installing an Omni IIe or OmniPro II control and security system.  The installer should also have thoroughly reviewed and understood the owner’s manual, which has important information regarding final setup of the system.  This manual assumes that the installer has a basic understanding of installing a security system.

This guide applies to the 20A00-2, -5, -22, -50, -51, and -52 versions of the Omni IIe and OmniPro II controller.  Refer to the Underwriters Laboratories Installation Requirements section for details in the application of each.  Failure to install the system and its accessories in accordance with the UL Requirements in this manual and in the owner's manual is a violation of the Listing Mark.

## PLANNING

Before you start, your system should be planned as follows:

- Zones:

- Decide where each contact or detector will be located

- Decide which zone it will occupy

- Decide zone type for each zone

- Decide which area it will occupy

- With the customer, decide what text and voice descriptors will be used.  Consult table of voice descriptors, so that you can choose similar words for the text to avoid customer confusion.

- See SMOKE DETECTOR INSTALLATION GUIDELINES to plan locations for smoke detectors

- Consoles:

- Consult the customer on the console location.  The console should be easily accessible.

- Interior Sounder and Outside Siren:

- Locate both where they cannot be tampered with.

- Lighting and Appliance Switches and Modules.

- Plan for thermostats, energy saver modules, or other options.

- Give consideration to where the controller will go.  Remember that it needs an electrical outlet not controlled by a switch, preferably on its own circuit, within 5 feet of the controller.

# INSTALLATION

Go over your plan with your customer.

- Install the entire system.  Refer to sections in this manual to see how to install various components.

- Follow the Power-Up and Checkout procedures.

- Explain the basics to the customer.  Deliver all manuals and documentation.

- Follow up with your customer to keep them satisfied.

## CONTROLLER HOOKUP

- When choosing a place to mount the controller, consider the following:

- An electrical outlet, preferably on its own circuit, is required to be within 5 feet of the controller for the power transformer and the UPB PIM or X-10 Interface Module.

- The controller should be protected from weather, temperature extremes, and burglars.

- GROUND THE CONTROLLER "EARTH GND" TERMINAL TO A COLD WATER PIPE OR TO A 4-FOOT GROUND ROD TO PRESERVE ITS BUILT-IN TRANSIENT PROTECTION.  USE 14 GAUGE WIRE.  TRANSIENT PROTECTION WILL NOT WORK IF THE CONTROLLER IS NOT PROPERLY GROUNDED.

- Connect the 24 VAC power transformer to the 24 VAC INPUT terminals.

- Connect the BLACK battery wire to the minus (-) terminal on the battery.  DO NOT connect the red wire at this time.  DO NOT reverse the connections; the battery fuse will blow.  Note that the unit will NOT START on the battery alone.

- Connect the Powerline Interface Module to the Omni series controller:

- UPB PIM (P/N: 36A00-1):  Plug one end of the 6-conductor modular cable into the connector marked “J3” (SERIAL 3) on the controller and plug the other end into the modular connector on the PIM.

- X-10 Interface Module (P/N: TW523): Plug one end of the 4-conductor modular cable into the connector marked “J7” (X-10) on the controller and plug the other end into the modular connector on the X-10 Interface Module.

- Refer to FIGURE 1 (CONTROLLER HOOKUP) for this configuration.

FIGURE 1 - CONTROLLER HOOKUP

## ABOUT SECURITY ZONES

Each of the security zone inputs on an Omni IIe (up to 48) and OmniPro II (up to 176) system may be configured as a burglary zone, a fire zone, a temperature zone, or an auxiliary input.  Zones 1-4, however, are the only inputs that can be used with 2-wire smoke detectors.  Zones 9-16 (on the controller) and Zones 49-176 (on expansion enclosures) are the only inputs that can be configured as a PESM.

An external 1000-ohm end-of-line zone resistor is required for all zones unless the Setup item ZONE RESISTERS is set to "No".  If the Setup item ZONE RESISTORS is disabled, all zones other than Supervised Fire and Gas (and all zone inputs on Expansion Enclosures) will not use an end-of-line resistor.  In this configuration, all zone switches (other than Supervised Fire and Gas) must be normally closed (open for alarm).  If any zone requires a normally open (closed for alarm) switch (other than Supervised Fire and Gas), the Setup item ZONE RESISTORS must be set to "Yes" and all zones will require and external 1000-ohm end-of-line resistor.

The zone type for each zone is selected through the INSTALLER SETUP menu or by using the PC ACCESS software.

The system supports a maximum zone resistance, excluding the end-of-line resistor, of 150 ohms.  The default setting for ZONE RESISTORS is "Yes".  The default settings for all zone inputs on an Omni series controller are configured as Auxiliary inputs.

The Omni IIe can be expanded to 48 zones by adding two 16 Zone Hardwire Expander Modules.  The OmniPro II controller can be expanded to 176 zones by adding two 16 Zone Hardwire Expander Modules and up to eight 16 Zone Expansion Enclosures or two Wireless Receivers.

### BURGLAR ZONE HOOKUPS

The Omni series system supports both normally open and normally closed switches.  Most contacts designed for doors, windows, motion detectors, glassbreak detectors and other security devices meet this requirement.  An external 1000-ohm end-of-line resistor must be used for all burglary zones if ZONE RESISTORS is set to "Yes".

- When using a normally open switch, a 1000-ohm end-of-line resistor must be in parallel with the zone being used.  Maximum loop resistance excluding end-of-line resistor should not exceed 150 ohms.  ZONE RESISTORS must be set to "Yes".

- When using a normally closed switch, a 1000-ohm end-of-line resistor must be put in series with the zone being used if ZONE RESISTORS are set to "Yes".  If ZONE RESISTORS are set to "No", the 1000-ohm end-of-line resistor is not used.  Maximum loop resistance excluding end-of-line resistor should not exceed 150 ohms.

Note: The 1000-ohm end-of-line resistor is required on all zone inputs on Expansion Enclosures.

- Power motion detectors from AUXILIARY 12V.

- Unused zones may be left open, and should be left at the default setting of AUXILIARY zone types.

- When Zones 1-4 are configured to anything other than a Supervised Fire or Gas zone, the corresponding Zone Jumpers (JP11-JP14) must be in the NRM (normal) position.

- See FIGURE 2 (OVERALL CONNECTIONS DIAGRAM) for configurations of burglary zones.

FIGURE 2 - OVERALL CONNECTIONS DIAGRAM

## ABOUT FIRE ZONES

The Omni IIe and OmniPro II system supports normally open (closed for alarm), two-wire or four-wire smoke detectors.  
Two-wire smoke detectors can only be connected to Zones 1-4.  Four-wire smoke detectors can be connected to any zone.  An external 1000-ohm end-of-line resistor must be used for all fire (and gas) zones.  When Zones 1-4 are configured as a Supervised Fire (two-wire or four-wire) or Gas zone, the corresponding Zone Jumpers (JP11-JP14) must be in the "SMK" (smoke) position.  Zone Jumper "JP11" corresponds to Zone 1, "JP12" corresponds to Zone 2, "JP13" corresponds to Zone 3, and "JP14" corresponds to Zone 4.

- Smoke detectors must be powered from SWITCH 12V or an Output configured as a SWITCHED POWER OUTPUT.

- End of line resistor: 1000 ohms.  Maximum loop resistance EXCLUDING end of line resistor is a 150 ohms.  Use HAI Model 1503A0011 End of Line Resistor Assembly in UL Listed Installations.

- Smoke detectors are reset when the security system is armed.

### TWO-WIRE SMOKE DETECTORS

The Omni IIe and OmniPro II controller supports two-wire smoke detectors connected to Zones 1-4.

- Use normally open (closed for alarm) two-wire "SYSTEM" type smoke detectors (See - 2-Wire Smoke Detector Compatibility Chart).

- Smoke detectors must be connected to Zones 1-4 and configured as a Supervised Fire Zone.

- An external 1000-ohm end-of-line resistor must be used.

- Connect to the SWITCH 12V or an Output configured as a SWITCHED POWER OUTPUT.

- The corresponding Zone Jumpers (JP11-JP14) must be in the SMK (smoke) position.

- Refer to FIGURE 3 (TWO-WIRE FIRE ZONE CONNECTIONS) for this configuration.

Smoke detector compatibility identifier: A

| Detector Models | Detector Manufacturer | Maximum Detectors/Zone |
| --- | --- | --- |
| 2W-B 2WT-B | System Sensor, Unincorporated Div. of Honeywell International Inc. | 10 |
| DS260 DS282 DS282S DS282TH DS282THS DS250 DS250TH | Bosch Security Systems | 10 |
| F220-P F220-PTH F220-PTHC DS230 DS230F | Bosch Security Systems | 8 |
| 429AT 521B (SW 1 “ON”) 521BXT (SW 1 “ON”) 521NB (6V) 521NBXT (6V) | GE Security Inc. | 10 |

2-Wire Smoke Detector Compatibility Chart

### FOUR-WIRE SMOKE DETECTORS

The Omni IIe and OmniPro II controller supports four-wire smoke detectors connected to any zone.

- Use normally open (closed for alarm) four-wire "SYSTEM" type smoke detectors (System Sensor 2112/24TR or equivalent), rated 8 - 14 VDC.

- An End of Line Power Supervision Relay Module (System Sensor A77-716B or equivalent) is required for UL installations.  Install 1000-ohm end-of-line resistor as shown.

- Power the smoke detector from SWITCH 12V or an Output configured as a SWITCHED POWER OUTPUT.

- When connected to Zones 1-4, the appropriate Zone Jumper (JP11-JP14) must be in the SMK (smoke) position.

NOTE:	Smoke detectors connected to Zones 1-4 are wired differently from those connected to Zones 5-176.  
Refer to FIGURE 4 (FOUR-WIRE FIRE ZONE CONNECTIONS) for each configuration.

FIGURE 3 - TWO-WIRE FIRE ZONE CONNECTIONS

FIGURE 4 - FOUR-WIRE FIRE ZONE CONNECTIONS

## TELEPHONE CONNECTIONS

- If an RJ31X jack has been supplied by the telephone company, it is probably wired correctly and the controller can be connected by plugging the supplied 8 conductor telephone cable into the RJ31X jack.  The other end of the cable is spaded.  The green, red, brown, and gray wires must be connected to the controller at the designated terminals under the section of the board marked 'PHONE'.

- If required, install the supplied RJ31X jack as shown in the following diagram.  The polarity must be correct for proper operation of the phone access feature.

- IT IS IMPERATIVE THAT THE PHONE LINE COMING INTO THE HOUSE BE CONNECTED TO A GROUNDED SURGE ARRESTOR OUTSIDE THE PREMISES.   IT IS THE RESPONSIBILITY OF THE TELEPHONE COMPANY TO PROVIDE THIS SURGE ARRESTOR.

- INSPECT THE INCOMING PHONE LINES.  THE FIRST THING THAT THEY SHOULD GO TO IS A SMALL BOX ON THE OUTSIDE OF THE PREMISES.  THERE SHOULD BE A HEAVY GROUND WIRE COMING FROM THIS BOX GOING TO A COLD WATER PIPE OR A SEPARATE GROUNDING ROD.

- IF THERE IS NO SURGE ARRESTOR OR IF THE GROUND WIRE IS MISSING, HAVE THE CUSTOMER INSIST THAT THE TELEPHONE COMPANY INSTALL ONE FOR THE SAFETY OF THE CUSTOMER.

- WHEN WIRING A RJ31X JACK, MAKE SURE THAT THE INCOMING PHONE LINES GO TO THE TELEPHONE COMPANY SURGE ARRESTOR BEFORE THEY GO TO THE RJ31X JACK.

- When the RJ31X is installed as shown, locate the green, red, brown, and gray spaded wires from the 8 conductor phone cable and connect to the section on the Omni series controller marked 'PHONE'.  Plug the modular end of the cable into the RJ31X jack.  If necessary, bend the tab up on the plug to ensure a tight fit that will not fall out.

- Verify the following if you have trouble during check out: With the system running, the RJ31X jack properly connected and all phones on-hook (hung up), the PHONE LED, located in the upper left corner of the controller, should be Off.  If it is on, reverse the RED and GREEN wires to both the house phones and the telephone company wires at the RJ31X jack.  When the receiver is picked up on any phone, the PHONE LED will come on.  When the phone line rings, the PHONE LED will light.

- If the Omni series system is accessed on an in house telephone, the Omni series controller will disconnect the phones from the phone company lines and supply its own talk voltage to the phones.  The PHONE LED will be on in this case.

- Refer to FIGURE 5 (RJ31X JACK CONNECTIONS) for this configuration.

### DIGITAL SUBSCRIBER LINE (DSL) CONNECTIONS

When the Omni series controller is connected to a Digital Subscriber Line (DSL), a DSL Splitter must be used to provide separate outputs for filtered voice (phone) and DSL (data).  Splitting the voice and data is necessary because:

- The higher frequencies of the DSL signal must not pass through the Omni series controller.  It can cause problems with the DTMF detection and the digital dialer.

- Whenever the Omni series controller is accessed on an in house telephone, the Omni series controller will disconnect the phones from the phone company lines (in this case the DSL line).  When that occurs, the DLS connection is temporarily lost.

Refer to FIGURE 6 (DSL SPLITTER CONNECTIONS) for this configuration.

FIGURE 5 - RJ31X JACK CONNECTIONS

FIGURE 6 – DSL SPLITTER CONNECTIONS

## LCD CONSOLE HOOKUP

- Omni II supports up to 8 and the OmniPro II supports up tp16 LCD Consoles (Models 33A00-1, 33A00-4, 11A00-1, 
11A00-2, 11A00-9, and 15A00) MAXIMUM per system, subject to power availability.

- Use 4-conductor 22-gage wire, 1000 feet maximum length.  Consoles can be homerun or daisy chained.  This length shall be divided by the total number of consoles at the end of the run.  For example, for 8 consoles, the maximum length reduces to 125 feet.  All LCD Consoles are connected to the same 4 wires, +12, GND, A, B.

- The console should be mounted so that the LCD display is at or slightly above eye level.  Consoles should be kept out of the reach of young children.  A good height is approximately 58 inches from the floor to the bottom of the console enclosure.

- Remove console face from back plate (slots on bottom of console will release back plate, use a screwdriver).  Mount the back plate to the wall.  Mounting holes are designed to fit on a single or double gang box, or directly to the wall.  Pull the wires from the wall through the opening in the back plate.  Splice the wires to the supplied cable.  Connect the cable to the connector on the console board (J1).  Snap the console face on to the back plate.  Remove protective film from the LCD lens.

- Refer to FIGURE 7 (CONSOLE CONNECTIONS) for this configuration.

## CONSOLE SETUP

The console has different operating options that can be setup from the console to the user's preference.  If more than one console is being used, it is required that you give each console a different address.  You can change the address of a console through the console setup mode.

To enter the console setup mode, simultaneously press and hold the 4 and up arrow () for approximately 1 second.  The console will beep 5 times and enter the setup mode.  The top line of the display will indicate what you are doing, followed by the current setting.  The bottom line will show a menu of your options.  To the lower right corner of the display is the direction arrow(s).  Where possible, the up (), down (), and two-headed () arrow characters are shown on the console display to indicate which arrow keys may be pressed at that time.  Press the down arrow () key to advance to the next item.  Press the up arrow () key to go back to the previous item.

### CONSOLE ADDRESS

If you are installing more than one console, each console must be set to a different address.  The default address setting is (1) - this is adequate if only one console is being used.  The choices at the bottom are 1-16.  When making your choice, choose an address between 1-8 for an Omni IIe and 1-16 for an OmniPro II, then press the # (pound) key.

### SOUNDER

If you wish not to hear the beeper in the console for any reason, the sounder option can be turned off.  Select (0) for OFF or (1) for ON, then press the # key.

### KEY CLICK

The sounder makes a click every time a key is pressed.  This option may also be turned off.  Select (0) for OFF or (1) for ON, then press the # key.

### KEY BACKLIGHT

The keys on the console keypad are lit.  The keys can be never lit, always lit, or only lit when the LCD display is lit.  Select (0) OFF, (1) for ON, or (2) TIMED, then press the # key.

### VIEWING ADJUSTMENT

This option is an adjustment for the viewing angle of the LCD display.  This has been set to its best value at the factory, however, you may wish to tweak it.  The display has 20 levels of adjustment.  Select (1) for a lower viewing angle, or (2) for a higher viewing angle.

### LANGUAGE

This option is to display the 'console setup' text on the LCD display in English, French, Italian, or Spanish.   Select one of the languages, then press the # key.

### EXIT SETUP MODE

To exit Setup Mode, press and hold the 4 and up arrow () keys simultaneously for about 1 second.  The console will return to normal operation.  You may need to press (*) to restore the display.

FIGURE 7 - CONSOLE CONNECTIONS

## SOUNDER OUTPUTS

The Horn Output provides 12VDC to power bells, piezo sirens, self-contained sirens, and siren drivers (do not connect speakers to the Horn Output).  Sounders can draw up to 1 amp MAXIMUM, split between the Interior and Exterior Horn Outputs  - (See Specifications for UL Ratings).  Use a relay connected to an auxiliary power supply if higher current draw is required.

### INTERIOR SOUNDER HOOKUP

- Locate the interior sounder in a central location.  The sounder is very loud.  Do not install it in a room where small children or animals could be trapped if the alarm is activated.

- The Interior Horn Output monitors the wiring to bells and sirens.  When enabled, it will report trouble and make a digital dial out when an open, short, or other wiring problem is detected in the supervised bell circuit.  When violated, the console display will indicate that there is a fire tamper trouble.

- For UL Listed residential fire alarm applications, the UL Listed Wheelock Model MT-12/24-R Multitone Signal or equivalent must be used, and the internal sounder must be supervised.

- Refer to FIGURE 8 (SOUNDER CONNECTION) for connections.

### EXTERIOR SOUNDER HOOKUP

- If used, wire tamper switches to a tamper zone with a 1000-ohm end-of-line resistor.

- The Exterior Horn Output monitors the wiring to bells and sirens.  When enabled, it will report trouble and make a digital dial out when an open, short, or other wiring problem is detected in the supervised bell circuit.  When violated, the console display will indicate that there is a fire tamper trouble.

- Refer to FIGURE 8 (SOUNDER CONNECTION) for connections.

FIGURE 8 - SOUNDER CONNECTIONS

## CONTROLLER OUTPUTS

The Omni IIe and OmniPro II controller provides 8 programmable hardwired voltage outputs and two horn voltage outputs.  These outputs are programmable for the following output types:

- General Purpose low voltage switching applications (12 VDC)

- Sounder triggering (a trigger for siren and voice drivers for BURG and FIRE)

- Communicator outputs (radio, cellular, or any other type of auxiliary communicator)

- 'ARMED' and 'OK TO ARM' outputs

- Switched Output (to power smoke detectors and cycle power to latching devices)

Outputs 1 - 8 can supply a maximum of 100 mA each.  These outputs are included in the total DEVICES load, which cannot exceed 1A.  If the Interior or Exterior Sounder is configured to an Output Type, the HORN outputs can supply a maximum of 1A.  HORN outputs are included in the total HORNS load, which can not exceed 1A.

## RESET OUTPUTS

Outputs 1-8 are protected from an overload condition.  If an overload condition occurs on an output, it will shut off (the output will supply 0V).  When this occurs, the "Output Fault" (D26) LED (marked "A" if Figure 9) will illuminate.  To reset the output, remove the device causing the overload condition, then press the "Reset Outputs" (S1) Switch (marked "B" if Figure 9).

FIGURE 9 - RESETTING CONTROLLER OUTPUTS

## OUTPUT APPLICATIONS

### GENERAL PURPOSE SWITCHING APPLICATIONS

This output will supply 12 VDC to the output terminal when its corresponding unit is ON.  This can be used to drive relays for many different applications, including switching sprinkler valves and low-voltage lighting.

### SOUNDER TRIGGERING

This output can be used as a trigger for siren and voice drivers.  When a driver requires a separate input for burglary and fire, you can configure this output to give a voltage trigger to the driver.  Also, each area can have its own sounder.

### COMMUNICATOR OUTPUTS

This output can be used for radio communications or any other type of auxiliary communications to augment the built-in digital and voice dialers.  Any communications device can be used with the Omni series controller, provided that it is powered by 12 VDC, has 12 VDC triggered inputs, and has 2 (or more) channels.

The 'Communicator' outputs are activated 3 seconds before the Omni series system dialer begins to dial either using its built-in digital dialer or voice dialer.

The following events will activate the BURG output: Burglar alarms (including panic zones), Auxiliary emergencies, Police emergencies, and Duress alarms.  Fire alarms and the fire emergencies will activate the FIRE output.

Note: The Interior and Exterior Fire Sounder generates 12VDC in a 3 pulse temporal pattern.

### "ARMED" AND "OK TO ARM"

ARMED: When the system is armed in any of the security modes (Away, Night, Day, or Vacation), this output is active.  It is typically used to activate a red LED to indicate that the system is 'armed'.

OK TO ARM: When all security zones are secure, no zones are bypassed, and the system is in the Off mode, this output is active.  It is typically used to activate a green LED to indicate that the system is 'ok to arm'.

### SWITCHED OUTPUT

This output is used to cycle power to latching devices when the system is armed.  This output will reset the smoke detectors when the system is armed after an alarm.

### HAI COMMUNICATING THERMOSTATS

When HAI RC-Series thermostats are used, Output 8 is used to communicate with up to 64 thermostats.  There is no need to configure this output when used with HAI thermostats.  It may be left at the default setting of "General Purpose".

## REMOTE ARM/DISARM SWITCH

- If desired, a remote keyswitch, keypad, or hidden arm/disarm toggle switch can be connected to the system.  The device should have a momentary close type switch.

- Configure one of the zone inputs as a KEYSWITCH INPUT zone.  A closure of the switch contacts will toggle the arming mode between Off and Away mode (Entry and Exit delays are still active).

- Configure one of the outputs as an "ARMED" and another output as an "OK TO ARM" output.  These outputs are used to activate a red or a green LED based on the state of the alarm system.  The "ARMED" and "OK TO ARM" outputs can supply a maximum of 100 mA each.  These outputs are included in the total DEVICES load, which cannot exceed 1 A.

- Refer to FIGURE 10 (REMOTE KEYSWITCH CONNECTION) for this configuration.

NOTE: In UL Listed Installations, the Listed Ademco Model 9789 keyswitch shall be used.

FIGURE 10 - REMOTE KEYSWITCH CONNECTIONS

## HAI THERMOSTATS

Omni IIe supports up to 4 and OmniPro II supports up to 64 HAI RC-Series Communicating Thermostats.  The controller can send commands to the thermostat to change mode, cool setting, heat setting, status of fan and hold, and other items.

Run a 3 (or 4) conductor wire from the HAI system to the thermostat location.  All thermostats on an HAI Home Control system are connected to GND, Zone +16 (+Z16), and OUTPUTS 8 - See Figure 11.

FIGURE 11 - HAI THERMOSTAT CONNECTIONS

## PROGRAMMABLE ENERGY SAVER MODULES

Programmable Energy Saver Modules may be connected to:

Controller:	Zone 9 and Output 1	through	Zone 16 and Output 8, respectively

Expansion Enclosures:	Zone 1 and Output 1	through	Zone 16 and Output 16, respectively

- Omni IIe can support 8 and OmniPro II can support up to 136 Programmable Energy Saver Modules (PESM).  Each PESM requires one security zone input and one controller output.  The zone input corresponds to the controller output (Zone 9 and Output 1 through Zone 16 and Output 8, respectively).  If Zone 9 is used, Output 1 must be used as its pair.

- When setup as an Energy Saver Zone Type (Type 80), the zone and unit (output) is used as a pair to read in temperature and control the setback temperature of the house.  Only zones 9-16 and 49-176 may be configured as an Energy Saver zone.

- Run a 4-conductor wire from the Omni series controller to each PESM.  Connect as shown in FIGURE 13 (PESM CONNECTIONS).

- The PESM should be mounted on an interior wall, preferably close to the HVAC thermostat.  Run a 2-conductor wire from the PESM to the thermostat.  Connect the PESM between the RED wire going to the thermostat and the RED terminal on the thermostat.

- Program the zone type for PESMs as a Type 80, Energy Saver.  It may also be programmed as a Temperature (Type 82), or Temperature Alarm (Type 83) for special applications.

NOTES ON HVAC SYSTEMS

- Description of the PESM

The PESM is a temperature sensor and control relay in a small enclosure that mounts near a central heating, ventilation, and air conditioning (HVAC) system thermostat.  The PESM allows the automation system to read the temperature of the area that the HVAC system controls.  The relay in the PESM is used to break the 24V RED wire between the thermostat and the HVAC system.  When the automation system is in setback mode and the actual temperature is between the LO and HI setpoints, the relay energizes to break the 24V red wire; hence, the HVAC system will no longer operate.

In heating season, when the actual temperature falls below the LOW setpoint, the automation system turns the relay in the PESM off, thus restoring power to the thermostat, allowing the thermostat to heat as it normally would under the control of the thermostat.  The PESM will cycle the thermostat on and off to maintain the LOW setpoint.

In cooling season, when the actual temperature rises above the HI setpoint, the automation system turns the relay in the PESM off and the thermostat will cool as it normally would under the control of the thermostat.  The PESM will cycle the thermostat on and off to maintain the HI setpoint.

The Red LED on the PESM will illuminate when the PESM is overriding the thermostat.  The Red LED will be off when the thermostat is working normally.

If the PESM is disconnected from the automation system, the relay will not energize and the HVAC system will operate normally, under the control of the thermostat.

- Standard Heating and Cooling Systems

The PESM is compatible with all mechanical thermostats.

- The PESM is also compatible with electronic thermostats that run totally on battery power.

- Heat Pumps

Programmable Energy Saver Modules are compatible with heat pumps, however, the savings gained by setting the heat pump back may be erased by the auxiliary heaters when the heat pump tries to recover from the setback.  A PESM will work best with heat pumps that have one or more of the following features:

- An outdoor temperature switch that prevents the auxiliary heat from coming on unless it is very cold outside.  This is sometimes called a "heat balance" switch.

- A thermostat that uses rate of rise to determine if auxiliary heat is necessary: The Enerstat Model DSL-450.  When recovering from setback, the thermostat runs the heat pump first.  It will run the auxiliary heat only if the rate of temperature rise is less than 6 degrees F. per hour.

- An alternative auxiliary heat source that is inexpensive (i.e. gas).

These features will avoid the use of auxiliary heat (usually an electric strip heater) which is more expensive than using the heat pump when recovering from setback.  In general, heat pumps take a longer time to recover from setback, so it may be advantageous to program a setback only for extended periods, such as a vacation.

## TEMPERATURE, OUTDOOR TEMPERATURE, AND HUMIDITY

When connected to the controller, the Model 31A00-1 (31A00-7 Extended Range) Indoor/Outdoor Temperature and Model 31A00-2 (31A00-8 Extended Range) Indoor/Outdoor Temperature and Humidity Sensor is used for sensing indoor temperature and/or reporting the relative humidity from 0 to 100 percent or for sensing the outdoor temperature and/or reporting the outdoor relative humidity.  The outdoor temperature can be displayed on the console, spoken over the telephone, or displayed on an HAI Communicating Thermostat.

- Each Temperature Sensor requires one zone input.  Each Humidity Sensor requires one zone input.

- Program the zone type as an Outdoor Temperature (Type 81), Temperature (Type 82), Temperature Alarm (Type 83),  for temperatures between 0o F - 120o F

- Humidity (Type 84), for humidity between 0% – 100%

- Extended Range Outdoor Temperature (Type 85), Extended Range Temperature (Type 86), and Extended Range Temperature Alarm (Type 87), for temperatures between -40o F - 120o F

- When mounting outdoors, plan to mount under an overhang or to the underside of an eave, otherwise known as the soffet, to protect it from direct sunlight and rain.  Run a 4-conductor wire from the Omni series controller to the selected location.

FIGURE 12 - TEMPERATURE / HUMIDITY SENSOR CONNECTIONS

FIGURE 13 - PESM CONNECTIONS

## BUILT-IN SERIAL PORTS

Omni II and OmniPro II controllers have 5 serial ports (J1-J5) built onto the controller (labeled SERIAL 1 - SERIAL 5, respectively).  The interface is a modular connector located in the upper left corner of the controller.

Each serial interface supports both RS-232 and RS-485 connections.  RS-232 is the standard for connections to most personal computers and related systems.  RS-485 can support greater wiring distances.  The default setting is RS-232.  To select RS-485, move the interface jumper (JP1-JP5) from the 232 to the 485 position.  The jumpers (JP1-JP5) are located below the modular serial port connectors (J1-J5).

To connect a serial port to a PC, use the HAI Model 21A05-2 Serial Cable Kit.  Plug one end of the cable into one of the modular serial port connectors on the controller.  Plug the other end into the Model 21A05-1 Communication Cable Adaptor (modular to DB-9 RS-232), which connects the Omni series controller serial port to the computer's DB-9 RS-232 port.

To make your own serial cable to connect to a PC, follow the diagrams (Figure 14 and Figure 15).  When making connections, be sure to correctly orient the cable as shown (with the tab on the modular cable facing up, make sure that the Yellow wire is at the top).  Connect the Yellow, Green, Red, and Black wires to the DB-9 connector as shown.  Also, on the DB-9 connector, connect Pins 1, 4, and 6 together and Pins 7 and 8 together.

FIGURE 14 - RS-232 CONNECTIONS

Built-In Serial Port Pin Out

1 - N/C

2 - Ground

3 - DCD

4 - TX (transmit)

5 - RX (receive)

6 - 12V +

FIGURE 15 - RS-485 CONNECTIONS

## BUILT-IN ETHERNET PORT

The Omni IIe and OmniPro II controllers have an Ethernet port (J6) built onto the controller (labeled ETHERNET).  The Ethernet port allows a device to connect to the Omni IIe or OmniPro II controller via a network (i.e. Ethernet, Internet) using a secure, encrypted communication link.  The Ethernet port transports HAI application-level packets containing Omni-Link serial protocol messages over IP.

### CONTROLLER IP ADDRESS, PORT NUMBER, AND ENCRYPTION KEY

The controller’s local IP address and port number set the local network parameters for the Omni IIe or OmniPro II controller.  The encryption key is used to establish a private, secure connection with the connected device.

The following Setup items can only be assigned and changed from an HAI console.  These items can not be assigned or changed via PC Access; although the IP address and port number may be viewed via PC Access:

### CONTROLLER IP ADDRESS

The controller’s local network IP address is used to identify the Omni IIe or OmniPro II controller on the network.  To view and assign the controller’s local network IP address, from the Set Up menu, press the 6 key.  Using the down arrow key (), scroll to the following menu item:

IP ADDRESS

192.168.0.101          

The format of the IP address is a 32-bit numeric address written as four numbers separated by periods.  An IP address has two components, the network address, and the host address.  The first two numbers (e.g. 192.168) represent the Class B network address and must be the same as the first two numbers of your local network.  The second two numbers (e.g. 0.101) identify a particular host on the local network and may be assigned at random as long as each device on the local network has a unique address.  Each number can be 0-255.  Enter the 1, 2, or 3 digit number followed by the “#” key to move to the next number.  After the 4th number has been entered, press the “#” key to store the IP address.

### CONTROLLER PORT NUMBER

The controller’s local network port number identifies the logical channel to the Omni IIe or OmniPro II controller.  For example, port 80 is used for HTTP traffic; the controller’s local network port number is used for Omni-Link traffic.  To view and assign the controller’s local network port number, from the previous Setup item (IP ADDRESS), press the down arrow key ().

PORT NUMBER         4369

0-65535                

In most installations, the default port number can remain the same.  Port numbers range from 0-65535.  To change the port number, enter the new port number followed by the “#” key to store the port number.  Port numbers 0-1024 are reserved for designated services and should not be used.

### ENCRYPTION KEY

Encryption and decryption of data between the Omni IIe or OmniPro II controller and the connected device is based on the Advanced Encryption Standard (AES) using a 128-bit cryptographic key.  A unique encryption key is randomly assigned to each Omni IIe and OmniPro II controller at the factory (no records of these keys are kept at the factory).  It may be left the same (recommended) or it may be changed as desired.  To view and assign the encryption key, from the previous Setup item (PORT NUMBER), press the down arrow key ().

ENCRYPTION KEY PT 1:

6F-1B-26-A2-FF-D9-E4-12

This key consists of 16 bytes (that is 16 2-digit values from 0-9 and/or the letters A-F).  It is entered into the controller in two parts (PT 1 and PT 2) consisting of 8 bytes each.  Enter the 2 digit value.  To enter the digits A-F, first press the “OFF” key, then press the 0-5 key respectively (i.e. A1 = OFF 0 1 and CB = OFF 2 OFF 1).  After the last digit (16th digit) has been entered, press the “#” key to store “PT 1” of the encryption key.  Press the down arrow key () to enter “PT 2” of the encryption key.

ENCRYPTION KEY PT 2:

DC-67-48-8F-D1-3A-EF-70

After the last digit (16th digit) has been entered, press the “#” key to store “PT 2” of the encryption key.

### ETHERNET CONNECTIONS

Use a standard network cable to connect the controller to a hub, switch, or router.  Use a network crossover cable when connecting the controller directly to the NIC card on a computer.

When connected to a switch or router, port forwarding must be configured.  Port forwarding sets up public services on your network. The Omni IIe and OmniPro II controller listens for all IP/UDP communications addressed to it on the specified UDP port number.  The router will forward all communications on the specified port to the Omni IIe or OmniPro II controller.

### CONNECTING TO NETWORK VIA PC ACCESS

To access the controller over the network via PC Access:

- Open a PC Access account file.

- Click Configure >> Network.

- If you are connecting from the local network, enter the controller’s IP address under “Network IP Address or Domain Name”.

- If you are connecting from the Internet, enter either the public IP address (the way to reach your local network via the Internet) or domain name (e.g. www.homeauto.com).

- Enter the port number that is configured for the controller.

- Select the Encryption tab.  Enter the two part encryption key as it is displayed on the console.

- Select OK.

- Click Communication >> Connect >> Network.  PC Access should change from “Off-Line” to “On-Line”.

FIGURE 16 - LOCAL NETWORK

FIGURE 17 - LOCAL / WIDE AREA NETWORK

If the controller is connected to the Internet via a dynamic IP address, to locate and communicate with the controller from remote locations over the Internet using HAI PC Access, you must subscribe to a Dynamic DNS (Domain Name Service).  Dynamic DNS is a service that maps your dynamic (changing) IP address to a static (permanent) hostname, allowing you to access your Omni IIe or OmniPro II controller over the Internet using your static hostname instead of an IP address.

A “client” program (typically provided by the Dynamic DNS provider) runs on a PC on your local network and is used to automatically update your Dynamic DNS provider with your current IP address.  Several router/switch manufacturers have embedded a Dynamic DNS client into their router firmware.   These devices work with several of the Dynamic DNS providers, including both free and commercial services.  These devices are especially beneficial because the router can be powered up all the time, so the dynamic update is always current and is handled by a single device (the router/switch) in the local network.  This allows you to locate and connect to the Omni IIe or OmniPro II controller without having a computer on the local network powered up and running.

# SYSTEM POWER UP PROCEDURE

- Carefully review hookups to the zones, grounds, sounders, and consoles.

- Disconnect 1 lead of both the interior and exterior sounders.

NOTE: Follow this power up procedure to verify proper operation of the power supply, battery charger, and low voltage cut out relay.

- The positive lead to the battery should be disconnected at this time.  Make sure that the red battery wire is not touching anything.

- Plug in the power transformer.

- The AC ON LED should illuminate.

- Within one minute, the STATUS LED should begin blinking at a rate of 1 blink per second.  This indicates that the Omni series controller processor and software are working.

- The PHONE LED should be Off (if all telephones are on-hook and the RJ31X jack is properly connected.

- Unplug the power transformer to kill the system.  Connect the red battery wire to the + (positive) battery terminal.  The system should not start.

- Plug in the power transformer.  The system should start.

- Unplug the power transformer.  The system should continue to run on the battery (the STATUS LED will continue to flash).

- Plug the transformer back in and secure it to the outlet.

## CONSOLE CHECK OUT

- The console(s) should be operating.  Press ' * ' to silence the trouble beeper if it is beeping.  Press OFF, 1, 1, 1, 1 (or the current User code) if the alarm is tripped.  If the consoles are not operating properly, make sure that no two consoles have the same address, and check the wiring.

- With all doors and windows closed and all motion detectors secure, the bottom line of the display should read SYSTEM OK.  If there are any trouble indications that occurred during installation, press ' * ' to acknowledge them and silence the beeper.

- Set the time and date by pressing the 9 key.  Enter the Master Code, then press the 2 key.

- The console should now show the time and date on the top line and "SYSTEM OK" on the bottom line.

## TELEPHONE CHECK OUT

- Verify that the Telephone Company surge arrestor is properly grounded.

- Verify that the incoming telephone lines are run to the surge arrestor first, then from the surge arrestor to the RJ31X jack, then from the RJ31X jack to the house phones.

- The PHONE LED, on the controller, should be off when the phones are hung up.

- Pick up an in-house phone, wait about 1 second, then press the ' # ' key.  You should hear the Voice menu on the phone.  If not, check to see that the RJ31X jack is properly wired and connected to the controller.  There should be no interference from the Telephone Company while the menu is being read over the phone.

- Record the owner's NAME and ADDRESS in the ADDRESS speech memory as shown in SETUP ADDRESS in the OWNER'S MANUAL (Press 8, 9, then 1111 or the current Master code to record the address).

NOTE: DO NOT record any TOUCH TONES in the ADDRESS!!

- Check that all in-house phones are working.

## BURGLAR ZONE CHECK OUT

- With all doors and windows closed and all motion detectors and security devices secure, the console display should read "SYSTEM OK".

- If any zones are abnormal, check your wiring.  If the battery indication is low, make sure that the battery is connected securely.  Give the battery a chance to charge.

- From the top-level display, have a partner go around the house and trip each sensor one at a time.  The display should indicate the correct zone as not ready when the zone is tripped, then return to "SYSTEM OK" when the zone is secured.  Be sure that the zone type indicated (ENTRY/EXIT, PERIMETER, ETC.) is correct for the zone being tested.

- If the zone being checked is armed, (i.e. PANIC or TAMPER type, which is always armed) the alarm will be activated.  Press OFF and 1111 or the current User code to silence the alarm, or bypass the PANIC and TAMPER zone(s) before you start.

- Reconnect the sirens.  Be sure that no one is standing near a siren.  Activate the alarm, and ensure that both the inside and, after a delay, outside sirens activate.

## FIRE ZONE CHECK OUT

- Press ' * ' to return the console to the SYSTEM OK indication.  Check the fire zone per the sensor manufacturer's instructions.  The fire alarm should be activated (pulsing interior sounder, exterior siren).

- Press ' * ' to silence the alarm.  The display will still indicate that the FIRE ZONE is in alarm.

- Press DAY or NIGHT or AWAY and the User code to arm the system, then OFF and the User code to disarm.  This arm/disarm cycle will reset the smoke detector.  If the cause for alarm (i.e. smoke) has cleared, the display will return to SYSTEM OK.

NOTE: Be sure that the DIAL OUT DELAY is long enough so that you can cancel the alarm before the system dials out.

## CUSTOMER CHECKOUT

After you have completed the system check out and everything works, be sure that the customer knows how to:

- Disarm/silence the system (OFF, 1111 or current User code).  HAVE THE CUSTOMER PRACTICE!

- Change the codes.

- Get the menu over the in-house phones.

## IN CASE OF TROUBLE

### CONSOLES

If you experience trouble that seems to be with a console, try disconnecting the console and running the console self test as described under CONSOLE HOOKUPS in this manual.  If the console does not run the self-test properly, it should be returned to HAI for repair.

"NO CONTROLLER DATA" or erratic operation of the LCD display could be a result of: A and B terminals connected backwards, poorly, or 2 or more consoles have the same address.

CONSOLE SELF TEST

Use the self test mode to verify the proper operation of the console.

- Disconnect the console from the controller.  Connect +12 and GND terminals to a 12-volt source (or a fresh 9-volt transistor battery.) The console beeper will beep twice per second, the LCD backlight and the keypad key will be lit, and the LCD will display "NO CONTROLLER DATA".

- Simultaneously press and hold the 7 and the down arrow () keys for approximately 3 seconds.  The beeper will beep 5 times, the LCD backlight and keypad backlight will turn off, and the display will clear.  The LED at the top right corner of the console will start to cycle through its different colors (red, green, yellow, then turns off).  At the end of each cycle the beeper will beep once.

- Press any key.  The LCD backlight and the keypad key backlight will turn on.

- Press the keys in the following order and verify that the appropriate character fills the screen.  0 - 9, *, #, AWAY (A), NIGHT (B), DAY (C), OFF (D),  (filled blocks), and  (blanks).

If this is successful, the console is good.  Simultaneously press and hold the 7 and down arrow () keys to exit the self test mode or disconnect power.

### CONTROLLER

Check the AC ON (bottom) LED.  If it is not lit, check for 24 VAC at the transformer connections.

Check the STATUS (top) LED on the controller board.  It should be blinking once per second, indicating the proper operation of the microprocessor and memory.  If not, try powering the system down by disconnect the power transformer and battery, then reconnect both.  The status light should begin blinking.

If the AC ON LED is on and the STATUS light is still not blinking, check the AUX +12 V with a DC voltmeter.  It should be 13.7 volts.  If not, make sure that there isn't too much load on the system.  Disconnect all loads.  If the STATUS LED still won't blink, there is a problem with the controller board and it must be returned to HAI for repair.

Phone line problems, or problems with the Omni series controller’s voice are usually the result of the RJ31X jack being improperly wired.  Check RJ31X jack wiring and polarity carefully, as described in TELEPHONE CONNECTIONS.

In the event that the controller is found defective, the controller board can be removed without disconnecting the entire wiring from their terminals.  The terminal strips can be removed from the controller board.  Then the controller (or processor board) can be repaired and reinstalled easily.

Follow this procedure for removing the controller board:

- If possible, upload the programs and configuration. (This will not be possible if the status LED isn't flashing or if you can't get the voice to work.)

- Unplug the power transformer.

- Disconnect the battery

- Disconnect the RJ31X modular cable at the jack!!  If you only disconnect it at the Omni series controller only, the house phones won't work.

- Disconnect the X-10 cable.  Disconnect the serial cable(s).  Disconnect Ethernet cable.

- Carefully remove the four terminal strips from the controller board.  Gently push down on terminal strip retention clips.  These clips are located on either end of the strip and 2 in the middle.  Slowly pull strip away from terminal block socket and secure.

- Remove 9 screws and washers; 3 on the top edge, 3 on the bottom edge, and 3 in the middle of the controller.

- Remove the controller board.

- Wrap the controller board with protective material and pack carefully.  HAI will not be responsible for returned items damaged due to inadequate packaging.

- Call Home Automation, Inc. with the serial number for a Return Authorization number to help us track your return.  Write the R. A. # on the outside of the package.

- Return the controller to Home Automation, Inc.  Please include your return address, any special shipping instructions and daytime phone number so that we can reach you if we have any questions.  Also include a brief description of the problem that you are having.

- INSTALLATION: follow the removal process in reverse.  Follow the POWER UP and CHECK OUT procedures in this manual.

- NOTE: When a controller is returned from being repaired, all setup and programming is lost.  The board is returned with the factory default setup and programming.

FOR HELP: Call HAI between the hours of 9:00 AM and 5:00 PM Central time, Monday - Friday, at (800) 229-7256.

# DIGITAL COMMUNICATOR

The Omni series controller digital communicator can use Contact ID, or Standard 4/2 or 3/1, (20 pps, 1800 Hz data, 2300 Hz handshake), or (10 pps, 1900 Hz data, 1400 Hz handshake), dual round compared format.  Any central station with modern equipment can receive these formats.  Compatible receivers are Ademco, Radionics, Osborne-Hoffman, Linear, FBI, and Silent Knight.  It is up to the installer to verify compatibility.  At the time of installation, the installer is required to verify compatibility and phone line seizure of the Digital Communicator.

If the digital dialer does not get a handshake signal from the central station 45 seconds after it begins dialing, it hangs up and tries again.  The dialer will try the FIRST PHONE NUMBER 5 times, then go to the SECOND PHONE NUMBER and try that 5 times.  After that, the system will indicate COMMUNICATIONS FAILURE on the console display and the digital communicator will not try again until another reportable event occurs.

The digital communicator will not dial out until the DIAL OUT DELAY has expired.  If the alarm is canceled prior to the expiration of the DIAL OUT DELAY, no transmission will take place.  After the DIAL OUT DELAY has expired, though, all alarm trips will be transmitted followed by a CANCEL code.

When the digital communicator is used, all voice dial outs will be delayed for five minutes after the expiration of the dial out delay to allow time for the central station to call the premises after an alarm code has been sent.  If the digital communicator is unable to successfully communicate with the central station, the user will be alerted to the trouble condition.  When the system status is requested using the voice, this condition is reported over the phone as "SECURITY PHONE MESSAGE" trouble.

Single Line Transmission Signal System Configuration

### DESCRIPTION OF CONTACT ID

Contact ID reporting allows very specific event codes to be sent to the central station.  A complete report takes under three seconds.  Contact ID reporting uses predefined event codes that allow the central station to quickly identify the condition being reported.  The specific security zone or user code is identified as part of the report.

For each event code transmitted, the report also includes an event qualifier that identifies whether the report is for a new event (such as a security zone trip), or a restoration of an event (such as a security zone no longer tripped).  Trouble conditions are reported, as well as restoration of these trouble conditions.  For security arming and disarming events, this event qualifier is also used to identify whether the report is for an arm or disarm.  The reporting format for Contact ID is listed in Appendix A in this manual.

When using Contact ID, the alarm codes and/or reporting format cannot be changed.  However, if the DCM code (under the 4/2 and 3/1 Alarm Code Formats) is set to “0” or “00”, then Omni series controller will not make a call to the central station to report that code when using Contact ID.

### DESCRIPTION OF 4/2 and 3/1 FORMAT

The 4/2 format consists of a four-digit account code, from 0000 to FFFF and a two-digit alarm code from 00 to FF.  When the digital communicator calls the central station receiver, the latter answers and sends a brief 2300 Hz tone or a 1400 Hz tone called a "Handshake" tone.  The digital communicator then reports digits of the account and alarm codes as bursts of either (1800 Hz) or (1900 Hz) tone; the digit 8 is represented by eight bursts of tone.  A message, or "round" consists of an account code and an alarm code.  Two rounds are sent, and two consecutive rounds must match at the receiver.  If they do, the central station receiver sends another brief 2300 Hz or 1400 Hz tone to acknowledge to the digital dialer that the message has been properly received.  If the rounds don't match, the receiver does not send the second tone and the digital dialer tries again, up to 5 times.  If the rounds are not acknowledged after 5 tries, the digital dialer hangs up and tries the entire call again.

The digital communicator can report alarm zone trips, alarm cancels, low battery, and fire zone trouble.  It may also be setup to generate an automatic test signal at periodic intervals.  The communicator may be setup to call second phone number using a second account number in the event that it is unable to communicate successfully using the first phone number and account.

The digital communicator is setup at the factory to transmit a code when the battery is low or trouble with the fire zone is detected.  If these codes are set to 0 or 00, no code will be sent when the trouble condition is detected.

Although the alarm codes can be changed, we recommend that the alarm codes setup at the factory be used to minimize the risk of installer error in programming the digital communicator.  Simply enter the phone numbers and account codes, then verify the alarm codes.

Older central stations may require a 3/1 format.  To use 3/1 format, both account numbers must be changed to 3 digit codes and EVERY alarm code must be changed to a 1-digit code.  Do not mix code lengths!

### OPENING AND CLOSING REPORTS

The Omni series system can send opening and closing reports by user to the central station.

When the system is disarmed by user code 1-16, the communicator can call the central station and report that the system was disarmed (opened) with the user code that was used.

When the system is armed by user code 1-16, the communicator can call the central station and report that the system was armed (closed) with the user code that was used.

If any other code or a method disarms the system (i.e. Code 17-99, Keyswitch, or Scheduled Program), the communicator will send a generic OPEN report to the central station.  The code that is sent is defined as OTHER OPEN.  If the system is armed by any other method other than one that requires a code (i.e. Quick Arm, Keyswitch, or Scheduled Program), the communicator will send a generic CLOSE report to the central station.  The code that is sent is defined as OTHER CLOSE.

# ZONE TYPES

ZONE TYPE	NUMBER	DESCRIPTION

ENTRY/EXIT				0	Entry/Exit

PERIMETER				1	Perimeter

NIGHT INT				2	Night Interior

AWAY INT				3	Away Interior

2X ENTRY DELAY			4	Double Entry Delay

4X ENTRY DELAY			5	Quadruple Entry Delay

LATCH PERIM				6	Latching Perimeter

LATCH NIGHT INT			7	Latching Night Interior

LATCH AWAY INT			8	Latching Away Interior

PANIC					16	Panic

POLICE EMERG			17	Police Emergency

SILENT DURESS			18	Duress

TAMPER				19	Tamper

LATCH TAMPER			20	Latching Tamper

FIRE					32	Fire

FIRE EMERG				33	Fire Emergency

GAS					34	Gas Alarm

AUX EMERG				48	Auxiliary Emergency

TROUBLE				49	Trouble

FREEZE				54	Freeze

WATER					55	Water

FIRE TAMPER				56	Fire Tamper

AUXILIARY				64	Auxiliary

KEY SWITCH				65	Keyswitch Input

ENERGY SAVER			80	Programmable Energy Saver Module

OUTDOOR TMP				81	Outdoor Temperature

TEMPERATURE			82	Temperature

TEMP ALARM				83	Temperature Alarm

HUMIDITY				84	Humidity

ER OUTDOOR TMP			85	Extended Range Outdoor Temperature

ER TEMPERATURE			86	Extended Range Temperature

ER TEMP ALARM			87	Extended Range Temperature Alarm

### LATCHING ZONE TYPES

When any device (other then FIRE or GAS) is connected to SWITCH 12V or a Switched Power Output, the zone must be configured as one of the latching zone typeS (latching perimeter, latching night interior, latching away interior, and latching tamper).  Latching ZONE TYPES ignore the status of that zone during power cycles.

Used primarily when the FIRE ALARM VERIFICATION feature is being used or if more than one area is being protected.  This type will ignore the status of LATCHING zones (i.e. Glassbreak Detectors) when the power is switched to reset devices.

### DESCRIPTION OF ZONE TYPES

ENTRY/EXIT

Entry/Exit zone types are intended for doors.  Entry/Exit zones are armed in security modes DAY, NIGHT, AWAY, and VACATION.  In DAY and AWAY modes, there is an entry delay (defined by ENTRY DELAY) on entry/exit zones to allow you to get into the house and turn off the alarm before it sounds.  In NIGHT & DAY INSTANT mode, there is no entry delay, so that the alarm sounds immediately if someone opens a door.

There are two special types of ENTRY/EXIT zones for use with garage doors, or doors that are far away from the control console.  They are called DOUBLE ENTRY DELAY and QUADRUPLE ENTRY DELAY zones.  These zones have double or quadruple the ENTRY DELAY to give you additional time to reach the console to disarm the system upon returning.

Only the ENTRY DELAY is extended on these zone types.  The EXIT DELAY is not extended.

If an ENTRY/EXIT zone is tripped first, all other zones will are delayed.

PERIMETER and LATCHING PERIMETER

Perimeter zone types are intended for windows and exterior doors not requiring an entry delay.  All PERIMETER zones are armed in security modes DAY, NIGHT, AWAY, and VACATION.  There is not an entry delay on a perimeter zones.  If a window or door on this zone is opened while the security system is in DAY, NIGHT, AWAY or VACATION mode, the alarm will sound immediately.  Latching Perimeter zones ignore the status of that zone during power cycles.

NIGHT INTERIOR and LATCHING NIGHT INTERIOR

Night interior zones are intended for motion detectors in areas where no one should be while you are sleeping in your home.  For example, if you have a two-story home and sleep upstairs, your downstairs motion detector(s) should be on a NIGHT INTERIOR ZONE.

Night interior zones are armed in security modes NIGHT, VACATION, and AWAY only.  There is no delay on a NIGHT INTERIOR zone.  Night interior zones are NOT armed in DAY or DAY INSTANT mode, so that you may move about freely in your home when the security system is in DAY or DAY INSTANT mode, while still having the windows and doors protected.  Latching Night Interior zones ignore the status of that zone during power cycles.

AWAY INTERIOR and LATCHING AWAY INTERIOR

Away interior zones are for areas of your home where no one should be while you are away.  In the previous example, your upstairs motion detector(s) should be on an AWAY INTERIOR zone.  AWAY INTERIOR zones are armed only when the security mode is AWAY.  Latching Away Interior zones ignore the status of that zone during power cycles.

PANIC, TAMPER, and LATCHING TAMPER

Panic and tamper zones are for emergency pushbuttons and tamper switches.  PANIC and TAMPER zones are always armed, even if the security mode is Off.  There are no delays on PANIC and TAMPER zones.  An emergency dial out is activated after the DIAL OUT DELAY.

TAMPER zones should be used for items such as gun cabinets and liquor closets.

LATCHING TAMPER ZONES ignore the status of that zone during power cycles.

POLICE EMERGENCY

This zone type activates the burglar alarm and sounder.  An emergency dial out is activated after the DIAL OUT DELAY.

DURESS EMERGENCY (SILENT DIAL OUT)

If you wish to have a button in your home that activates a SILENT dial out, (no lights flashing and no sounder) it should be connected to a zone that is configured as a DURESS EMERGENCY.  If this zone is accidentally tripped, you will not know that the Omni series controller is making a silent dial out, and hence won't know to stop it.

To stop a silent dial out once it has started, you must go to the console and press OFF then enter your code.

SUPERVISED FIRE

Any zone can be programmed as a Supervised Fire ZONE.  In UL Listed Installations, all fire detectors must be configured as a Supervised Fire ZONE and connected as shown in this manual.  When Zones 1-4 are configured as a Supervised Fire ZONE, the corresponding Zone Jumpers (JP11-JP14) must be in the "SMK" (smoke) position.

FIRE EMERGENCY

This zone type activates the fire alarm for a normally closed (open for alarm) and open collector (short to ground for alarm) switches.  It is not supervised as required for UL Listed Installations and shall NOT be used in such installations.

GAS

This Gas ZONE will generate an alarm, activate the sounder (on - off - on - long off), and make a dial out.  This zone type requires an external 1000-ohm end-of-line resistor. When Zones 1-4 are configured as a GAS ZONE, the corresponding Zone Jumpers (JP11-JP14) must be in the "SMK" (smoke) position.

AUXILIARY EMERGENCY

This Auxiliary Emergency zone type will generate an alarm (console beeper - no sirens) and make an emergency dial out when the zone is violated.  An emergency dial out is activated after the DIAL OUT DELAY.

TROUBLE

This zone type can be used to monitor the status of an external device, such as the battery status of a wireless security receiver.  It can also used to record events in the event log (i.e. driveway activation, opening of a gate, etc.) without setting off the alarm.

When the zone is tripped, the zone name will be displayed on the display as "NOT RDY".  The alarm is not activated, regardless of the security mode.  The trouble is logged in the event log.  The digital communicator (if used) will report the alarm code for the zone.  The voice dialer will not be activated.

FREEZE

This Freeze alarm zone type will generate an alarm (console beeper, no sirens) and make an emergency dial out.

WATER

This Water alarm zone type will generate an alarm (console beeper, no sirens) and make an emergency dial out.

FIRE TAMPER

This zone type is used to monitor the wiring to bells and sirens (other than those connected to the HORN Output).  The zone will report trouble if an open, short, or other wiring problem is detected in the supervised bell circuit.  This zone will make a digital dial out when violated.  Connect a wire from the Fire Tamper zone (+) to an output configured as a Sounder.

AUXILIARY

A zone defined as AUXILIARY is ignored for security.  It is used to activate macros or to conditionalize programs.  This is the default setting for all zones.  Zones that are not in use should be configured as AUXILIARY.

KEYSWITCH INPUT

This zone is used to arm AWAY and Disarm the Omni series security system using a toggle (to ground) keyswitch or keypad.

PROGRAMMABLE ENERGY SAVER MODULE

This zone type is for use with the Programmable Energy Saver Modules (PESM).  It converts the Zone and the corresponding Output to operate the PESM.  Only Zones 9-16 can be programmed as a PESM.

OUTDOOR TEMPERATURE AND ER OUTDOOR TEMPERATURE

Use this zone type for Outdoor Temperature Sensors.  The outdoor temperature can be displayed on the console, spoken over the telephone, or displayed on an HAI Communicating Thermostat.

TEMPERATURE AND EXTENDED RANGE TERMPERATURE

The general-purpose temperature zone type is typically used to monitor indoor temperatures and control devices.  It sets the zone secure/not ready state for program conditionals and event button activation programs.

If FREEZE ALARM is enabled, it reports a potential freeze condition if the temperature falls below 40o.

TEMPERATURE ALARM AND EXTENDED RANGE TEMPERATURE ALARM

The temperature alarm zone type will generate an alarm (console beeper, no sirens) and dial out if the temperature goes above the high setpoint or drops below the low setpoint.

HUMIDITY

The HUMIDITY ZONE type is used to monitor indoor and outdoor humidity levels from 0 to 100 percent using the Model 31A00-2 Indoor/Outdoor Temperature and Humidity Sensor.  It sets the zone secure/not ready state for program conditionals and event button activation programs.

NOTE ON TEMPERATURE AND HUMIDITY ZONE TYPES

Outdoor temperature, temperature, and temperature alarm zone types all have HEAT (LOW) and COOL (HIGH) setpoints.  The zone is "Not Ready" when the temperature is above the high setpoint or below the low setpoint.  The zone is "Secure" when the temperature is between the setpoints.  Setting a setpoint to 0 disables the setpoint.

Except for a type 83 and 87, the alarm is not activated.  The zone "Not Ready" or "Secure" status is used to activate button programs and program conditionals.

# MISCELLANEOUS

To configure the miscellaneous Installer Setup items, from the Installer Setup menu, press the 6 key.

### INSTALLER CODE

The Installer code allows the installer access to the Installer Setup menu.  The Installer code should be changed and not given to the customer.  The Installer code cannot be used for remote phone access.

The default setting for the Installer code is 1 1 1 1.

NOTE:

Remember this Installer code and do not disable.  There is no way to reset or retrieve the code!  If the code is forgotten or disabled, the Omni series controller must be sent back to the factory.  Call for an RA#.

### ENABLE PC ACCESS

This enables or disables the PC ACCESS feature.  Factory default is enabled.

### PC ACCESS CODE

This code allows dealers to put an access code in the system that is separate from the customer's Master code and the Installer code.  Dealers can use the PC Access code to access the system by PC.  The PC Access code cannot arm and disarm the system.  The PC Access code is NOT programmed from the factory.  To use it, set it to any code other than 0000.  To disable the PC Access code, enter 0000 for the code.

NOTE:  This item must be enabled (by entering a code) if PC Access is will be used.

### RESET SYSTEM EEPROM

Select the 1 (YES) key to reset the EEPROM.  All programs, names, and setup items will be reset.  All system RAM will also be initialized and the system will restart.  This option, if effect, allows the system to be restored to factory fresh configuration.

### RESET SYSTEM RAM

Select the 1 (YES) key to cause all of the system RAM to be reinitialized.  The time, date, and event log will be cleared.  Other volatile memory locations will also be reinitialized.  The system RAM should only be reset if the system is acting strangely and memory corruption is suspected.  Resetting the system RAM will not reset any setup items stored in EEPROM.

### ETHERNET MAC ADDRESS

The Ethernet MAC Address, short for Media Access Control address, is the hardware address that uniquely identifies an Omni IIe or OmniPro II when connected to a network.

# EXPANSION

To configure each Expansion Module that is installed on the system, from the Installer Setup menu, press the 7 key.

Expansion Modules include Hardwire Zone Expanders, ALC Interface Modules, and Serial Interface Modules.

### MODULE 1 TYPE

The Module Type defines the function of each expansion module on the controller.  Module 1 is the module with the “ADDR” jumper set to 1.  Set the module type from the list below.  Press ' # ' to change the module type, then use the arrow keys to select the proper module type, then press ' # ' to enter.

MODULE 1 TYPE          1

NOT USED        #=CHNG 

For example, when configuring the module for a Hardwire Expander and if the jumper on the Hardwire Expander is set to 1, set “Module 1” Type to “1” (HARDWIRE EXPNDR).

MODULE TYPES	NUMBER	DESCRIPTION

NOT USED				0	No module is installed

HARDWIRE EXPNDR			1	Model 10A06 Hardwire Expander installed

ALC					2	ALC Interface Module is installed

OMNI-LINK				3	Model 10A17 Serial Interface using the Omni-Link protocol

PRO-LINK				4	Model 10A17 Serial Interface using the Pro-Link protocol

UPB					5	Model 10A17 Serial Interface using the UPB protocol

RADIO RA				6	Model 10A17 Serial Interface using the RadioRA protocol

NUVO CONCERTO			7	Model 10A17 Serial Interface using the NuVo Concerto protocol

CENTRALITE				9	Model 10A17 Serial Interface using the CentraLite protocol

VIZIA RF Z-WAVE			10	Model 10A17 Serial Interface using the Z-Wave protocol

HAI HI-FI				11	Model 10A17 Serial Interface using the HAI Hi-Fi protocol

NUVO ESSENTIA/SIMPLESE		13	Model 10A17 Serial Interface using the NuVo Essentia/Simplese protocol

XANTECH				14	Model 10A17 Serial Interface using the Xantech protocol

ACCESS CONTROL			18	Model 10A17 Serial Interface using the HAI Access Control protocol

HOMEWORKS				20	Model 10A17 Serial Interface using the Lutron HomeWorks protocol

CLIPSAL C-BUS			21	Model 10A17 Serial Interface using the Clipsal B-Bus protocol

Notes:

- Only 2 Model 10A06 Hardwire Expander Modules can be installed.

- Omni IIe supports 1 and OmniPro II supports 2 ALC Interface Modules.

- Only 1 Serial Interface Module can be installed.

- NuVo Concerto, NuVo Essentia/Simplese,  Xantech, and HomeWorks is only supported on the OmniPro II.

- The NuVo Grand Concerto, Speakercraft, or Proficient audio system can not be connected to the HAI Model 10A17 Serial Interface Module.  It must be connected to the (J2 Serial - J5 Serial) built-in serial port on the OmniPro II controller.

### MODULE 2 TYPE - MODULE 4 TYPE

Module 2 is the module with the jumper set to 2, and so on.  Set each module type from the list of “Module Types”.

### SERIAL 1 RATE

"Serial 1 Rate" selects the baud rate used for the first built-in serial interface (J1 Serial) on the Omni series controller.  Select the baud rate for the first built-in serial interface from the list.  Use the arrow keys to select the baud rate then press the ' # ' key.

### SERIAL 1 FUNCTION

The "Serial 1 Function" selects the communication protocol used for the first built-in serial interface (J1 Serial) on the Omni series controller.  Select the function for the first built-in serial interface from the list.  Use the arrow keys to select the function then press the ' # ' key.

FUNCTION TYPES	NUMBER	DESCRIPTION

OMNI-LINK	3	Serial communication using the Omni-Link protocol

PRO-LINK	4	Serial communication using the Pro-Link protocol

UPB	5	Serial communication using the UPB protocol

RADIO RA	6	Serial communication using the RadioRA protocol

NUVO CONCERTO	7	Serial communication using the NuVo Concerto protocol

RUSSOUND	8	Serial communication using the Russound protocol

CENTRALITE 	9 	Serial communication using the CentraLite protocol

VIZIA RF Z-WAVE	10	Serial communication using the Z-Wave protocol

HAI HI-FI	11	Serial communication using the HAI Hi-Fi protocol

NUVO GC/ESSEN G	12	Serial communication using the NuVo Grand Concerto or Essentia G protocol

NUVO ESSEN/SIMP	13	Serial communication using the NuVo Essentia/Simplese protocol

XANTECH	14	Serial communication using the Xantech protocol

SPEAKERCRAFT	15	Serial communication using the Speakercraft protocol

PROFICIENT	16	Serial communication using the Proficient protocol

ACCESS CONTROL	18	Serial communication using the HAI Access Control protocol

RUSSOUND E-SER	19	Serial communication using the Russound E-Series (Sphere) protocol

HOMEWORKS	20	Serial communications using the Lutron HomeWorks protocol

CLIPSAL C-BUS	21	Serial communications using the Clipsal C-Bus protocol

Notes:

  - NuVo Concerto, Russound, NuVo Grand Concerto, Nuvo Essentia/Simplese, Xantech, Speakercraft, Proficient, Russound E-Series, and HomeWorks is only supported on the OmniPro II.

  - The NuVo Grand Concerto, Speakercraft, or Proficient audio systems can not be connected to the first built-in serial port 
(J1 Serial) on the OmniPro II controller.  It must be connected to the (J2 Serial - J5 Serial) built-in serial port on the 
OmniPro II controller.

### SERIAL 2 - SERIAL 5 RATE

"Serial 2 Rate" - “Serial 5 Rate" selects the baud rate used for the second, third, fourth, and fifth built-in serial interface ports 
(J2 Serial - J5 Serial, respectively) on the Omni IIe and OmniPro II controller.  Select the baud rate for the built-in serial interface from the list.

### SERIAL 2 FUNCTION

The "Serial 2 Function" selects the communication protocol used for the second built-in serial interface ports (J2 Serial) on the Omni IIe and OmniPro II controller.  Select the function for the built-in serial interface from the list.

### SERIAL 3 FUNCTION

The “Serial 3 Function” by default is set to UPB to utilize HLC Lighting.  When using HLC, plug the HAI Powerline Interface Module (PIM) into the third built-in serial interface (J3 Serial) on the Omni IIe and OmniPro II controller.  To change the “Serial 3 Function”, select the function for the built-in serial interface from the list.

### SERIAL 4 - SERIAL 5 FUNCTION

The "Serial 4 Function" and "Serial 5 Function" selects the communication protocol used for the built-in serial interface ports 
(J4 Serial and J5 Serial, respectively) on the Omni IIe and OmniPro II controller.  Select the function for the built-in serial interface from the list.

Notes:

- Omni IIe only supports the Hi-Fi audio system.

- Omni IIe and OmniPro II controllers connect to the Clipsal C-Bus Serial PC Interface using an HAI Model 36A05-4 Serial Connectivity Adapter Kit.

- OmniPro II only supports communications with one audio distribution system.  Do not configure more than one audio protocol.

- The NuVo Grand Concerto, NuVo Essentia G, Speakercraft, or Proficient audio systems can not be connected to the first built-in serial port (J1 Serial) on the OmniPro II controller.  It must be connected to the second or third built-in serial port 
(J2-J5 Serial).

- When connecting the NuVo Grand Concerto or Essentia G audio system, the second built-in serial port (J2 Serial) is recommended.

- When connecting the Speakercraft audio system to the OmniPro II:

  - The Speakercraft RSA 1.0 MZC Control Interface Module must be used.

  - Use the HAI Model 21A05-2 Serial PC Cable for making the connection.

  - In order for the key presses to perform the correct operation, an MKP keypad must be assigned to address zero in each zone.

- When connecting the Proficient audio system to the OmniPro II:

  - Use the HAI Model 21A05-2 Serial PC Cable for making the connection.

  - In order for the key presses to perform the correct operation, a PMK keypad must be assigned to address zero in each zone.

- When connecting the NuVo Concerto, NuVo Essentia, NuVo Simplese, Russound CAV or CAM, or Xantech MRC-88 audio system to the OmniPro II, use the HAI Model 36A05-4 Serial Connectivity Cable for making the connection.

- When connecting the NuVo Grand Concerto or Essentia G audio system, an RS-232 Line Booster or Optical Isolator must be used (see HAI Knowledge Base article http://kb.homeauto.com/default.asp?id=849&SID=&Lang=1).

.

### SERIAL 6 RATE

"Serial 6 Rate" selects the baud rate used when a Serial Interface Module is added to the Omni IIe or OmniPro II system.   If a Serial Interface Module is installed, select its baud rate then press the ' # ' key.

# SPECIFICATIONS

Size:  Controller:  13 W x 13 H x 4.5 D

Console:   4.6 W x 4.5 H x 1.2 D

Weight:  Controller:  approx. 10 lb.

Console:     approx. 0.5 lb.

Operating     32 - 122 degrees F (0 - 50 degrees C)

Ranges:       10 - 95 % relative humidity, non-condensing

Power:        120 VAC, 60 Hz, 60 watts

Transformer:  24 VAC, 1.67 amps, 40 VA

Battery:      Rechargeable Lead-Acid, 12 volts, 7 amp-hour

Device Fuse:  Polyfuse:  1.35 A

Horns Fuse:   Polyfuse:  1.35 A

Battery Fuse: Polyfuse:  4.00 A

Polyfuses are permanent fuses that do not need replacement.

Nominal Voltage:       10 - 13.7 VDC, 0.5 V max. peak to peak ripple

Low Voltage Cut Out:   approx. 9 VDC

Typical Current Consumption at Nominal Voltage:

Controller:  135 mA

Console: backlight off - 35 mA; backlight on - 100 mA

Controller Maximum Group Current Outputs:

Devices:   AUX 12 VDC, SWITCH 12 VDC, CONSOLE, and OUTPUTS 1 - 8: 1 A

Horn:      INT HORN and EXT HORN: 1 A

Controller Maximum Individual Current Outputs:

Devices:   (Do not exceed 1 A total)

AUX 12 VDC                        1 A

SWITCH 12 VDC                     1 A

CONSOLE                           1 A

OUTPUTS 1 - 8                     100 mA

For 24-Hour Battery Standby Time, the following must be observed: (See Figure 18)

Controller Maximum Group Current Outputs (applies to residential and commercial):

Devices:   AUX 12 VDC, SWITCH 12 VDC, CONSOLE, and OUTPUTS 1 - 8: 250mA

Horn:      INT HORN and EXT HORN: 300mA

# UNDERWRITER'S LABORATORIES (UL) INSTALLATION REQUIREMENTS

The Omni IIe and OmniPro II control units are suitable for household burglar and fire applications.  Refer to UL1641 for installation requirements.

- The line carrier (X-10) operation is considered supplementary.  Operation of the line carrier devices was not investigated by UL.

- For those zones programmed as PANIC, DURESS or POLICE EMERGENCY, the initiating device shall be a UL Listed Hold Up Device switch.

- Connections to phone circuit must be made via the supplied cable and RJ31X Jack as shown under RJ31X JACK CONNECTIONS in this manual.

- For connection of smoke detectors to the controller, refer to requirements under FIRE ZONE HOOKUP and FIRE ZONE CONNECTIONS diagrams in this manual.

- The controller must be configured for 24 hour Standby Time as shown under 24 HR STANDBY CONNECTIONS diagram in this manual.  Maximum current ratings for 24 hours must be observed.

- Recognized energy limited cable shall be employed, 22 AWG minimum for all connections.

- The audible signal appliance shall be the Listed Wheelock Model MT-12/24-R Multitone Signal, rated 10.5 - 15.6 VDC, 95 dB(A) with 2 reflecting planes. The audible signal shall be mounted indoors in a central location.  The audible signal appliance can be connected to either the "INT HORN" or "EXT HORN" circuits.  In the case of the latter, the OUTSIDE SIREN DELAY shall be set to 0 seconds.

- For Residential Applications, the Model 10A01-1 Enclosure shall be used.

- For Commercial Applications, the Model 10A02-2 Commercial Enclosure shall be used.

- For Commercial Applications, Listed Ademco AB12 Bell and housing to be used.

- If the remote arm/disarm switch is used, it shall be the Listed Ademco Model 9789.

- Operation of the controls with the Programmable Energy Saver Module was not conducted by UL.

- Operation of the Model 12A00 Wireless Receiver was not verified by UL.

- Operation of the Two-Way Audio Module was not verified by UL.

- RS-232 and RS-485 communications were not verified by UL.

- Refer to the Owner's Manual for programming requirements in UL Listed Installations.

- For the monitoring of burglar alarm initiating devices, the zone type shall provide an audible output (i.e., not DURESS).

- The Omni controller must be connected (when employed) to listed carbon monoxide gas detectors (i.e. Sentrol -Model 240-CO).

- All connections to energy sensors and modules must be done to listed Class 2 circuits only.

- The Omni IIe and OmniPro II must be used in Residential Applications that are under a single ownership.

When used in UL Listed Installations, the following items apply:

- The "High Security Mode" must be ON.

- The "Enable Auto Bypass" feature must be OFF.

- The "Zone Resistors" must be YES.

- The "Supervise Int Horn" must be YES.

- The ENTRY DELAY SHALL NOT EXCEED 45 SECONDS for Residential Applications; 60 seconds for Commercial Applications.

- The EXIT DELAY shall not exceed 60 seconds.

- Double Delay and Quad Delay zone types shall not be used.

- The BEEP ON TROUBLE feature must be ON.

- For Residential Applications the sounding device may be mounted indoors.  If, however, the sounding device is connected to the "EXT HORN" terminals of the Omni IIe and OmniPro II, then the OUTSIDE SIREN DELAY shall be set to 0.

- The DIAL OUT DELAY shall not exceed 30 seconds.

- The SWINGER SHUTDOWN feature for each zone must be NO.

- The CROSS ZONING feature for each zone must be NO.

- The EXIT TIME RESTART feature must be NO.

Installer:      NAME:  __________________________________            NUMBER:  _______________________________

# 24-HOUR STANDBY BATTERY CAPACITY

Maximum current ratings for 24-hours:

Aux 12 VDC, Switch 12 VDC, Console, and Outputs 1-8: 250 mA

Interior Horn and Exterior Horn: 350 mA

FIGURE 18 - 24-HOUR STANDBY CONNECTIONS

# SMOKE DETECTOR INSTALLATION GUIDELINES

- Ceiling mounted smoke detectors should be located in the center of the room or hall, or not less than 4 inches from any wall.  When the detector is mounted on a wall, the top of the detector should be 4 to 12 inches from the ceiling.

- Do not install smoke detectors where normal ambient temperatures are above 100 deg. F (37.8 deg. C) or below 40 deg. F (4 deg. C).  Also, do not locate the detector in front of air conditioners, heating registers, or other locations where normal air circulation will keep smoke form entering the detector.

- Additional information on Household Fire Warning is available at nominal cost from: The National Fire Protection Association, Battery March Park, Quincy, MA. 02269.  Request Standard No. NFPA 72.  Contact your home Insurance Company for a possible reduction of your insurance premium.

- A smoke detector should be located between the sleeping area and the rest of the family living unit.

- In family living units with more than one sleeping area, a smoke detector should be provided to protect each sleeping area.

- A smoke detector should be located on each story (Refer to the diagrams below).

- For complete details on proper location and installation of smoke detectors, refer to the instructions supplied with the smoke detector.

# APPENDIX A – CONTACT ID REPORTING FORMAT

| ZONE TYPE | TRIP | TROUBLE | DESCRIPTION |
| --- | --- | --- | --- |
| Entry/exit (also Double & Quad) | 134 | 370 | Entry/exit burglary |
| Perimeter (also Latching) | 131 | 370 | Perimeter burglary |
| Night Interior (also Latching) | 132 | 370 | Interior burglary |
| Away Interior (also Latching) | 132 | 370 | Interior burglary |
| Panic | 120 | 375 | Panic alarm |
| Police Emergency | 120 | 375 | Panic alarm |
| Silent Duress | 122 | 375 | Silent panic |
| Tamper (also Latching) | 137 | 370 | Tamper burglary |
| Fire | 110 | 373 | Fire alarm |
| Fire Emergency | 110 | 373 | Fire alarm |
| Gas | 151 | 373 | Gas alarm |
| Auxiliary Emergency | 150 | 370 | 24 hour non-burglary |
| Trouble | 330 | 330 | System peripheral trouble |
| Freeze | 159 | 370 | Low temperature alarm |
| Water | 154 | 370 | Water leakage |
| Auxiliary | none | 370 | Auxiliary trouble |
| Fire tamper | 321 | 321 | Bell/siren #1 trouble |
| Temperature Alarm | 152 | 370 | Refrigeration alarm |

| EVENT | CODE | DESCRIPTION |
| --- | --- | --- |
| Zone bypass/restore | 570 | Zone bypass/restore |
| Fire zone bypass/restore | 571 | Fire bypass/restore |
| Automatic communicator test | 602 | Periodic test |
| Cancel | 406 | Cancel |
| User disarm/arm | 401 | Open/close by user |
| Programmed disarm/arm | 403 | Automatic open/close |
| PC Access disarm/arm | 407 | Remote open/close |
| Quick arm | 408 | Closing-quick arm |
| Keyswitch disarm/arm | 409 | Keyswitch open/close |
| Recent closing | 459 | Recent closing |
| Exit error | 374 | Exit error |

| SYSTEM TROUBLE | CODE | DESCRIPTION |
| --- | --- | --- |
| Battery low | 302 | Low system battery |
| Fuse | 312 | Power supply overcurrent |
| AC power failure | 301 | AC power loss |
| Phone line dead | 351 | Phone line #1 trouble |
| Digital communicator | 350 | Communication failure |
| Fire tamper | 321 | Bell/siren #1 trouble |

HAI   •   New Orleans, LA   •   U S A

# Text boxes

To connect to an Omni IIe or OmniPro II controller on a local network using HAI PC Access, under Configure >> Network enter the controller’s IP address:

(i.e. 192.168.0.101)

To connect to an Omni IIe or OmniPro II controller from the Internet using HAI PC Access, under Configure >> Network enter the public IP address:

(i.e. 134.42.112.8)

To connect to an Omni IIe or OmniPro II controller on a local network using HAI PC Access, under Configure >> Network enter the controller’s IP address:

(i.e. 10.0.0.230)